## Slide 1: Using DOASA to investigate recent trends in the NZ electricity market’s management of dry years
Presented to EPOC Winter Workshop
July 2014

## Slide 2: Motivation
2009 Ministerial Review
Electricity Industry Act 2010
To examine impact of measures on management of dry years
We studied 2008, 2012 and 2013

## Slide 3: Measures undertaken
Sale of Whirinaki
Reserve energy scheme abolished
Customer Compensation Scheme
Scarcity pricing
Stress testing
Physical asset swaps between SOEs
Virtual asset swaps between SOEs
Electricity futures market

## Slide 4: DOASA
Variant of the SDDP algorithm
Aims to optimise the scheduling of hydro and thermal generation resources in the face of uncertain future inflows
Developed by Stochastic Optimization Limited
A version is available as part of the Authority's suite of EMI tools

## Slide 5: Stagewise dependence of inflows (1)
    Physical inflows exhibit stagewise dependence
    Inflows in one period partly depend on inflows in earlier periods
    Important in order to correctly account for the probability of dry (and wet) sequences

## Slide 6: Stagewise dependence of inflows (2)
    Some SDDP implementations use linear Periodic Autoregressive (PAR) models to represent stagewise dependence
    DOASA approximates this by artificially spreading (increasing variance of) inflows
    Dependent Inflow Adjustment (DIA) feature automatically spreads inflows for each catchment consistent with accumulation over a specified number of weeks

## Slide 7: Water Values
DOASA yields marginal water values for each hydro storage reservoir
Function of reservoir storage and date
Represent the expected value of holding back a unit of water for release in some future period
And hence the opportunity cost of instead releasing that unit of water now
Balance risk of spill and running out of water

## Slide 8: Two approaches used
    Compare the water values implied by actual reservoir levels (under various hydro policies) with the prices that actually occurred
    Simulate operation with actual inflows (under various hydro policies) and compare simulated reservoir levels with the levels that actually occurred

## Slide 9: Implied water values approach
    Water values depend on model inputs (thermal prices and shortage prices)
    Somewhat subjective
    Tuning factors required to match market prices
    We chose to scale the demand
    Manually spread inflows – 2x
    Observed trends are interesting

## Slide 10: Simulated reservoir levels approach
    Depend more on relativity between water values and thermal/shortage prices
    Actual prices less important
    Less dependent on market dynamics
    More objective
    Model risk aversion by adding one or more fictitious dry years when creating policies
    DIA accumulation over 4 weeks

## Slide 11: Implied water values

## Slide 12: Water values vs spot price 2008: Spreading factor 2; 110% Demand

## Slide 13: SI water values vs SI storage 2008: Spreading factor 2; 110% Demand

## Slide 14: Water values vs spot price 2012: Spreading factor 2; 120% Demand

## Slide 15: SI water values vs SI storage 2012: Spreading factor 2; 120% Demand

## Slide 16: Water values vs spot price 2013: Spreading factor 2; 120% Demand

## Slide 17: SI water values vs SI storage 2013: Spreading factor 2; 120% Demand

## Slide 18: Best fit
    2008 – 110% demand
    2012 & 2013 – 120% demand
    Implies market was more risk averse in 2012 and 2013 than in 2008

## Slide 19: Other observations
    Spot prices move ahead of the movement in model water values
    Market is anticipating movements in storage to some extent
    Better information than the model?
    Partly due to stagewise dependence?

## Slide 20: Simulated reservoir levels

## Slide 21: Simulation results 2008: One fictitious dry year policy

## Slide 22: Simulation results 2008: Three fictitious dry year policy

## Slide 23: Simulation results 2012: One fictitious dry year policy

## Slide 24: Simulation results 2012: Three fictitious dry year policy

## Slide 25: Simulation results 2013: One fictitious dry year policy

## Slide 26: Simulation results 2013: Three fictitious dry year policy

## Slide 27: Closest match (Total NZ storage)
    2008 – One fictitious dry year policy
    2012 & 2013 – Three fictitious dry year policy
    Again implies market was more risk averse in 2012 and 2013 than in 2008

## Slide 28: Other observations
    Individual reservoir levels depart from the simulated levels much more than the aggregated level …

## Slide 29: Lake Pukaki and Lake Tekapo (1)
    Lake Pukaki and Lake Tekapo in 2008
    Both lakes controlled by Meridian
    Actual levels quite similar
    SPECTRA? - lumped island reservoirs
    Heuristic to split out reservoir policies
    Model runs Lake Tekapo almost empty!
    Tekapo directly supplies 185MW of plant
    Pukaki directly supplies 1550MW of plant

## Slide 30: Lake Pukaki and Lake Tekapo (2)
    Similar pattern in 2012
    After Tekapo stations sold to Genesis
    Not so obvious in 2013
    Disrupted by canal outages?

## Slide 31: Lake Hawea
2008 - Lake Hawea drawn down rapidly
Almost empty through July – August
Contact under-hedged?
2012 – lower inflows April through August
Yet more gradual draw down
Contact better positioned?
Model holds Hawea high (valuable)
Only 13% of Clutha inflows are controllable
Compare: Waitaki 70%; Waikato 77%

## Slide 32: Lakes Manapouri/Te Anau
Model runs lakes lower than in reality
Operating rules allow temporary excursions above main operating range
Model has hard limit at top of main operating range
Hence model overstates risk of spill
Should model a higher limit to better approximate the rules

## Slide 33: Some questions
Management of individual reservoirs under the market deviates markedly from DOASA’s supposedly optimal strategy
Does this imply a loss of welfare?
How material is it?
Would a greater range of hedge products better align individual company incentives with total welfare maximisation?
What sort of products?

## Slide 34: How much risk aversion is “optimal”?
    Theoretically a risk neutral policy has the lowest expected cost
    This should be the case over a very large number of Monte Carlo simulations (with inflow spreading)
    This approximates the population the policy is optimised for
    But …

## Slide 35: Expected cost of 2008 policies 400 Monte Carlo simulations

## Slide 36: Why did risk neutral policy not minimise cost?
    Algorithm was terminated after 300 iterations so not completely converged?
    400 Monte Carlo simulations - not a large enough statistical sample to approximate the entire population?

## Slide 37: What about historical simulations?

## Slide 38: Expected cost of 2008 policies Historical simulations

## Slide 39: Expected cost of 2012 policies Historical simulations

## Slide 40: Expected cost of 2013 policies Historical simulations

## Slide 41: Observations
    Even “worse” than Monte Carlo
    Significant load shedding cost for risk neutral policy
    Risk neutral policy clearly not optimal

## Slide 42: Why?
    Inflow spreading technique not adequately accounting for risk of extended dry sequences?
    82 historical inflow sequences only a small sample of entire population
    Reduced set of 20 historical inflow years used to generate policies did not adequately capture some of the driest historical sequences in full 82 year set?

## Slide 43: So how much risk aversion is “optimal”?
    2008 & 2013 – load shedding avoided and cost minimised for one fictitious dry year policy
    2012 – load shedding avoided and cost minimised for two fictitious dry year policy
    But 2012 & 2013 simulations look like a three fictitious dry year policy (best match)
    Implication: market might be overly risk averse now?

## Slide 44: Conclusions
  Market appears significantly more risk averse since Authority’s security of supply measures
  Market managed 2012 and 2013 dry year events more effectively than in 2008
  Maybe industry as a whole is now treating hydro risk a little too conservatively?
  Management of individual hydro reservoirs appears to deviate significantly from welfare maximising strategy
  Perhaps new hedge products would help this

## Slide 45: Questions … ?