## Slide 1: Analysing renewable power system development for a Pacific Nation
Ramu Naidoo (Scientia Consulting)
E Grant Read (EGR Consulting)
in association with Concept Consulting Group

## Slide 2: Study: for World Bank
Analysed the economics of a proposed hydro project in the Solomon Islands considering:
  system requirements
  current diesel generation
  solar and battery resources
  interplay between energy and reserves
We discuss some challenges of modelling this small system:
  And some observations on renewable development
The Global Infrastructure Facility (GIF) is a global collaborative platform that facilitates preparing and structuring complex PPPs in infrastructure and mobilizing capital from the private sector and institutional investors. For more information, please visit www.globalinfrafacility.org

## Slide 3: Honiara – Solomon Islands

## Slide 4: Current Power System
Demand profile consistent through the year
Current peak ~ 16MW
Predominantly diesel supply
Existing solar ~1MW
Ageing diesel generation fleet
Largest diesel unit: 4.5MW
Smallest diesel unit: 1.5MW

## Slide 5: Potential resources
Hydro (3 or 4 x 5MW units)
  Variable inflows
  Limited storage (~ 1 day with average inflows)
Solar
  Variable output
Batteries
  Energy and reserves
Geothermal (not considered as part of this exercise)
  Baseload energy

## Slide 6: Expected increase in oil prices
Source: EIA and World Bank

## Slide 7: Declining solar/battery technology costs
Source: Utility-Scale Solar, 2015, Lawrence Berkley National Laboratory
Source: IRENA, 2015

## Slide 8: Modelling framework
An optimisation modelling framework was developed for this specific system
It optimises at three nested levels with outputs from preceding levels fed forward
Optimal thermal dispatch model
Least-cost hydro-thermal-solar-battery dispatch model
Least-cost development plan model

## Slide 9: Some caveats
Hydro option and data as provided by SIEA, World Bank, and other consultants
3% discount rate (with sensitivities at 4%) – based on World Bank requirements
Assessment only on generation (ignoring transmission)
Optimistic assumptions about power system control etc from new technologies (implying conservative valuation of hydro)

## Slide 10: Hydro with existing system
Current system predominantly diesel with some solar
  Diesel fuel prices linked to global oil prices
  Ageing diesel units
  ~1MW of existing solar
Proposed hydro development would be large proportion of system demand (sometimes exceeding)
Hydro can displace diesel but need to consider the interactions:
  High and low inflows
  Energy and reserves

## Slide 11: High inflows – hydro energy production limited by load
Limited storage implies spill when load cannot fully absorb hydro generation
Spill
Spill
Initially off-peak loads lower than hydro capacity

## Slide 12: Reserve requirements further restrict hydro generation
Also need to manage contingencies
Need more reserves to cover shortfall
Spare hydro can provide reserves
Hydro gen reduced to supply load
Reduce hydro gen further
Reserves from hydro and diesel
Provision of reserves reduces hydro energy

## Slide 13: Low inflows – hydro only provides reserve and peak support
Hydro generation limited under low inflows  reduce peak of residual load curve  reserve provider

## Slide 14: Surprisingly?
Under these assumptions, optimisation recommends batteries to support hydro generation
  During low load periods
  By avoiding need to back-off hydro and/or run additional diesel for reserves
Battery reserves cover shortfall
Spare hydro can provide reserves
Hydro gen reduced to supply load
Battery reserves

## Slide 15: Ancillary service batteries
High power – short duration application
Keep system going while reserve Diesels are started

## Slide 16: Energy-shifting batteries
Shift energy/capacity from lower-priced periods to higher-priced periods
Capture excess energy and use to displace higher-priced generation (e.g. diesel)
Battery charging when surplus generation
Online diesel to provide reserves for solar fluctuation

## Slide 17: Solar – no hydro
Can displace diesel generation:
  More on sunny days
  Less on cloudy days
  None at night
Still need diesel to cover series of dark days
Online diesel, or batteries, required to manage short-term solar fluctuations
But “energy shifting” batteries offer no gains while diesel is on the margin all day:
  Only worth considering when solar penetration is so high that excess solar would otherwise “spill”, on sunny days.

## Slide 18: Solar – with hydro
Hydro can complement solar in displacing diesel generation:
  Increased energy during wet conditions
  Increased reserves during dry conditions
Hydro will compete with solar during periods when diesel is completely displaced
  Wet and sunny - compete
  Wet and cloudy - complement
  Dry and sunny - complement
  Dry and cloudy - complement
Significant Diesel capacity still required for backup over dry periods with successive cloudy days

## Slide 19: An integrated system development
Hydro build
Diesel to manage dry periods and dark days
Increasing solar as costs reduce
Initially ancillary service batteries to support hydro with reserves
Energy batteries to capture excess solar

## Slide 20: Can we go 100% renewable?
System must sustain itself over successive dry cloudy days without backup diesel
Limited hydro energy used for overnight generation
Batteries capture excess solar and complement hydro generation over daily cycle
Significant solar overbuild required, with energy spilled most of the time.
    Get up to 8 hours charging time on dry dark days
    With discharge of up to 16 hours over peak/night period
Can save money with mix of short/long term batteries,
    And sensible design of solar infrastructure

## Slide 21: Optimisation for renewable case
Large increase in system costs in doing away with diesel backup generation  increased value of hydro capacity

## Slide 22: Conclusion
Small scale makes analysis comparatively more costly
  But also arguably more complex
In a small isolated system it becomes critical to capture the salient interactions of:
  Energy and ancillary services
  Unit loading patterns and contingencies
  Short and long term output variability and storage/backup capacity
The interacting characteristics of different technologies can create a complex pattern of competition and complementarity, over time
Diesel capacity seems likely to play an important ongoing backup role
  And is btw “100% renewable”, if not actually called upon!